## Slide 1: February 2021 winter storm event
Presentation to NASUCA
Paul Suskie
Executive Vice president & General Counsel
Southwest Power Pool
Updated 5/10/21

## Slide 2: 2021 winter Storm grid emergency

## Slide 3: SPP REGION IN COLDEST part of u.s.
ERCOT
MISO
PJM
NYISO
ISO-NE
CAISO
SPP
* Locations of ISOs/RTOs are approximate

## Slide 4: Operations data

## Slide 5
Participating Entity | % of MW
CSWS | 16.8
WAPA | 13.5
SPS | 12.4
OKGE | 12.4
KCPL | 9.68
WR | 8.49
NPPD | 6.57
OPPD | 4.6
WFEC | 3.78
GRDA | 2.22
SECI | 2.22
EDE | 2.19
LES | 1.36
SPRM | 1.22
KACY_N | 0.92
CBPC | 0.83
INDN | 0.38
SPA | 0.28
TSGT | 0.13
SPP Total | 100%
Interruptions by entity
Chart: Load Shed MW
| 2/15/2021 1:00 | 2/15/2021 2:00 | 2/15/2021 3:00 | 2/15/2021 4:00 | 2/15/2021 5:00 | 2/15/2021 6:00 | 2/15/2021 7:00 | 2/15/2021 8:00 | 2/15/2021 9:00 | 2/15/2021 10:00 | 2/15/2021 11:00 | 2/15/2021 12:00 | 2/15/2021 13:00 | 2/15/2021 14:00 | 2/15/2021 15:00 | 2/15/2021 16:00 | 2/15/2021 17:00 | 2/15/2021 18:00 | 2/15/2021 19:00 | 2/15/2021 20:00 | 2/15/2021 21:00 | 2/15/2021 22:00 | 2/15/2021 23:00 | 2/16/2021 | 2/16/2021 1:00 | 2/16/2021 2:00 | 2/16/2021 3:00 | 2/16/2021 4:00 | 2/16/2021 5:00 | 2/16/2021 6:44 | 2/16/2021 7:00 | 2/16/2021 7:17 | 2/16/2021 8:00 | 2/16/2021 9:00 | 2/16/2021 9:32 | 2/16/2021 10:00 | 2/16/2021 11:00 | 2/16/2021 12:00 | 2/16/2021 13:00 | 2/16/2021 14:00 | 2/16/2021 15:00 | 2/16/2021 16:00 | 2/16/2021 17:00 | 2/16/2021 18:00 | 2/16/2021 19:00 | 2/16/2021 20:00 | 2/16/2021 21:00 | 2/16/2021 22:00 | 2/16/2021 23:00
Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610 | 610 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1359 | 1359 | 2718 | 2718 | 2718 | 1359 | 1359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
610 MW
(~1.5% of BA Load)
2,718 MW
(~6.5% of BA Load)
1359 MW
(~3.2% of BA Load)
Required interruptions were allocated to transmission operators on pro-rata basis

## Slide 6
available Generation in SPP Market
Average Available Generation
Extreme weather reduced available generation by ~20 GW below historical Feb. average

## Slide 7
GENERATING CAPACITY OUTAGES
Energy Emergency Alerts in Effect
Fuel Oil
During peak conditions,
gas generation contributed to ~60% of total unavailability
Wind generation outages ~5x more than first week of Feb

## Slide 8: Total GENERATING Capacity in SPP
2/16 EEA3
2/15 EEA3
Available generation during EEA3 periods constituted ~65% of accredited capacity.

## Slide 9: Generating Capacity in SPP – Coal
2/16 EEA3
2/15 EEA3
Coal generation during EEA3 periods constituted ~80-82% of accredited capacity.

## Slide 10: Generating Capacity in SPP – Gas
2/16 EEA3
2/15 EEA3
Gas generation during EEA3 periods constituted ~42-48% of accredited capacity.

## Slide 11: Generating Capacity in SPP – Wind
2/16 EEA3
2/15 EEA3
Wind generation during EEA3 periods constituted ~90-115% of accredited capacity.

## Slide 12
Energy that met Demand in Real-Time Market
2/16 EEA3
2/15 EEA3
SPP relied on energy from multiple sources, including imports from neighbors

## Slide 13: Natural Gas Prices

## Slide 14: Natural gas hub prices
Chart: Day-ahead natural gas ($/MMBtu)
| 44235 | 44236 | 44237 | 44238 | 44239 | 44240 | 44241 | 44242 | 44243 | 44244 | 44245 | 44246 | 44247 | 44248 | 44249
Henry Hub | 3.49 | 3.4 | 3.35 | 3.755 | 6.5 | 6.118 | 6.118 | 6.118 | 6.118 | 11.318 | 23.86 | 8.56 | 4.962 | 4.962 | 4.962
NNG Ventura | 3.835 | 4.052 | 4.056 | 7.245 | 15.613 | 102.973 | 102.973 | 102.973 | 102.973 | 178.24 | 16.781 | 6.048 | 3.806 | 3.806 | 3.806
Delivery So Star | 3.582 | 3.75 | 3.9 | 9.961 | 45 | 300 | 300 | 300 | 300 | 265.5 | 90 | 7.591 | 4.409 | 4.409 | 4.409
NGPL Forgan OK | 3.605 | 3.377 | 3.471 | 4.932 | 12.45 | 238.692 | 238.692 | 238.692 | 238.692 | 389.231 | 19.984 | 6.522 | 4.066 | 4.066 | 4.066
NGPL TX-OK | 3.25 | 3.206 | 3.2 | 3.706 | 6.963 | 11.566 | 11.566 | 11.566 | 11.566 | 143.5 | 26.322 | 6.181 | 4 | 4 | 4
ONG at Tulsa | 3.463 | 3.697 | 4.186 | 8.65 | 27.5 | 377.129 | 377.129 | 377.129 | 377.129 | 935.5 | 1065.5 | 13.122 | 3.562 | 3.562 | 3.562
PEPL | 3.466 | 3.44 | 3.689 | 6.8 | 17.832 | 210.062 | 210.062 | 210.062 | 210.062 | 109 | 28.333 | 5.91 | 3.85 | 3.85 | 3.85
Waha Hub | 3.165 | 3.164 | 3.275 | 5.285 | 12.5 | 157.714 | 157.714 | 157.714 | 157.714 | 209.753 | 77 | 8.5 | 4.25 | 4.25 | 4.25

## Slide 15: Natural gas supply dropped significantly
https://www.eia.gov/todayinenergy/detail.php?id=46896
Notes: During the cold snap that affected much of the central part of the country, U.S. dry natural gas production fell to as low as 69.7 billion cubic feet per day (Bcf/d) on February 17, a decline of 21%, or down nearly 18.9 Bcf/d from the week ending February 13. Natural gas production in Texas fell almost 45% from 21.3 Bcf/d during the week ending February 13 to a daily low of 11.8 Bcf/d on Wednesday, February 17, according to estimates from IHS Markit. Temperatures in Texas averaged nearly 30 degrees Fahrenheit lower than normal during the week of February 14.
The decline in natural gas production was mostly a result of freeze-offs, which occur when water and other liquids in the raw natural gas stream freeze at the wellhead or in natural gas gathering lines near production activities. Unlike the relatively winterized natural gas production infrastructure in northern areas of the country, natural gas production infrastructure, such as wellheads, gathering lines, and processing facilities, in Texas are more susceptible to the effects of extremely cold weather. https://www.eia.gov/todayinenergy/detail.php?id=46896

## Slide 16: Communications

## Slide 17: SPP Balancing authority Operations: Feb. 4-20, 2021
Time blocks are not to scale
Thurs. 2/4 to Mon. 2/8
Tues 2/9 to Sat. 2/13
Mon. 2/15
Tues. 2/16
Thurs. 2/18
Fri. 2/19
Sat. 2/20
Normal operations in effect
Tues. 2/9: Declared conservative operations until further notice
Thurs. 2/11: Began to commit generating resources multiple days in advance for Sat. 2/13 to Tues. 2/16
Sat. 2/13: Reminded market participants of emergency cap & offer processes
Requested member companies issue public appeals for conservation
Declared EEA1 to be effective 2/15 at 05:00
05:00 Declared EEA1
07:22 Declared EEA2
10:08 Declared EEA3 New record peak
12:04 - Demand interruption
13:01 - EEA3
14:00 Declared EEA2
EEA2 in effect
10:07 – EEA3
11:30 Declared EEA2
12:31 Declared EEA1
18:28 Declared EEA2
EEA 2 in effect
13:15
Declared EEA1
18:20 Declared EEA2
22:59
Declared EEA1
Conservative operations in effect
EEA1 in effect
09:30
Ended EEA and remained in conservative operations through 22:00 Sat. 2/20, with appeal for public conservation
18:25 – Declared EEA1
EEA1
in effect
09:20 Ended EEA and remained in conservative operations through 22:00 Sat. 2/20, with appeal for public conservation
Conservative operations in effect
22:00 Declared normal operations
06:15 Declared EEA3
06:44
Demand interruption
Sun. 2/14
Wed. 2/17
Mon. 2/8: Issued resource alert to grid operators: “Implement resource preparations…ensure resource commitment start-up and run times ...report fuel shortages & transmission outages…”
Thurs. 2/4: Issued cold weather alert to grid operators

## Slide 18: Next Steps

## Slide 19: After the storm
Collaborate with members and industry to ensure region is equipped to manage future crises effectively
Comply with FERC and NERC inquiries
Review processes for improvement areas
Document lessons learned